## sheet-1
Flow Control Commune |  | Control Valve Specification Sheet
Chennai, India
Customer |  | Customer_2 |  |  |  | Quote No | 501
Project |  | 1 |  |  |  | FCC W/O No | 0
End User | [5 empty] | Serial No | N/A
RFQ No | [5 empty] | Tag No | 111
PO No | [5 empty] | Qty | 1
P & ID Ref / Line No | [5 empty] | Item No. | 10
Fluid State / Name |  | Liquid |  |  |  | Critical Pressure |  | 100 | bar
Service Description |  | Mixing |  |  |  | Shutoff Pressure |  | 275.5
AA | Valve Sizing Calculation | Units | Case1 | Case2 |  | Case3 | Case4 | Case5 |  | Case6
1 | Flow Rate | m3/hr | 1000 | 1000 |  | 1000
2 | Inlet Pressure | bar | 10 | 10 |  | 10
3 | Outlet Pressure | bar | 9 | 9 |  | 9
4 | Inlet Temperature | C | 30 | 30 |  | 30
5 | Specific Gravity |  | 0.85 | 0.85 |  | 0.85
6 | Kinematic Viscosity | centipose | 1000 | 1000 |  | 1000
7 | Vapor Pressure | bar | 0.1 | 0.1 |  | 0.1
8 | Liquid Pr. Recovery Factor, Fl |  | 0.647 | 0.626 |  | 0.66
9 | Calculated Cv |  | 1279.524 | 1276.459 |  | 1295.559
10 | Percentage Opening / Degree | % | 64 | 64 |  | 64
11 | Noise level at 1m distance | dB | 63.54 | 63.6 |  | 63.64
12 | Inlet Pipe Velocity | m/s | 8.609 | 8.609 |  | 8.609
13 | Outlet Pipe Velocity | m/s | 8.609 | 8.609 |  | 8.609
14 | Trim Exit Velocity | m/s | 0.277 | 0.277 |  | 0.275
15 | Warnings!!
BB | Pipe Line Data |  |  |  | EE | Actuator Data
16 | Size, Schedule Inlet | 8 | inch |  | 45 | Actuator Type |  | Spring & Diaphragm
17 | Size, Schedule Oulet | 8 | inch |  | 46 | Actuator Model No. / Travel |  | /1.5
18 | Insulation |  |  |  | 47 | Actuator Size / Spring |  | 105.0
19 | Design Pressure | 10 |  |  | 48 | Air Fail Action |  | AFO
20 | Design Temp. Min / Max | 30 |  |  | 49 | Air Supply / Set pressure |  | 80/60.0
CC | Valve Body & Bonnet |  |  |  | 50 | Actuator Orientation |  | none
21 | Valve Mfg / Model No.. | 10-1301 |  |  | 51 | Handwheel |  | Side Mounted
22 | Size / Rating | 8 | inch | 150 | 52 | Travel Stops
23 | Body Style | globe |  |  | 53 | Tubing make / Size
24 | Body Material | RPTFE |  |  | 54 | Fittings
25 | End Connections | None |  |  | 55 | Open / Close / Trip Time
26 | End Finish / Preparation | N/A |  |  | FF | Accessories & Tubings
27 | Body F/F Dim |  |  |  | 56 | Positioner Mfg / Model
28 | Bonnet Type | Standard |  |  | 57 | Signal Action
29 | Bonnet Material | ASTM A216 WCB |  |  | 58 | AFR Make / Model
30 | Extension dimension |  |  |  | 59 | Position Transmitter
31 | Body/Bonnet NDE1 | None |  |  | 60 | Limit switch / Proximity switch
32 | Body/Bonnet NDE2 | None |  |  | 61 | Boosters
33 | Bonnet Bolting | None |  |  | 62 | Pilot Valves
34 | Gasket Material | Standard for Service |  |  | 63 | Air Lock Relay
35 | Gland Packing |  |  |  | 64 | I/P converter Make / Model
DD | Valve Trim |  |  |  | 65 | Solenoid Valve Make / Model
36 | Trim Size / Type | Ported |  |  | 66 | Solenoid Action
37 | CV/Characteristic | 1281.062 |  |  | 67 | Volume Tank
38 | Balancing | UNBALANCED |  |  | GG | Testing, Certification, Cleaning, Painting
39 | Flow Direction | over |  |  | 68 | Testing-1
40 | Trim Material | 316 SS |  |  | 69 | Testing-2
41 | Soft Seat Material | None |  |  | 70 | Testing-3
42 | Seat Leakage Class | ANSI Class II |  |  | 71 | Product Certification
43 | Bellows Material |  |  |  | 72 | Assembly cleaning procedure
44 |  |  |  |  | 73 | Painting Specification
HH | Notes | [7 empty] | Revison Control
74 | N1- MPI-Body/Bnt Castings/Forgings to ASME B16.34 at Foundry/Forge | [7 empty] | By | Rev. | Date
75
76
77
78
79
80
81
82
83
QMS/AE/002